## Slide 1: Updates from hydesign V0 to V1

## Slide 2: The major updates from hydesign V0 to V1 include:
P2X model and sizing
More efficient EGO algorithm
Exercise notebooks
A more accurate battery degradation model
Long term EMS to take into account degradation of PV and battery

## Slide 3: Evaluation results comparison Site: France good wind site
We run model evaluations for the three designs, and compare the evaluation results between the two versions:
100% of the grid in Wind capacity
100% of the grid in PV capacity
50% Wind + 50% PV + 3h (20% grid in battery MW) )

## Slide 4: Evaluation results comparison Site: France good wind site
 | Design 1 NEW | Design 1 OLD | Design 2 NEW | Design 2 OLD | Design 3 NEW | Design 3 OLD
longitude | 0.864258 | 0.864258 | 0.864258 | 0.864258 | 0.864258 | 0.864258
latitude | 48.744116 | 48.744116 | 48.744116 | 48.744116 | 48.744116 | 48.744116
altitude | 302.0 | 302.0 | 302.0 | 302.0 | 302.0 | 302.0
Clearance [m] | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0
sp [m2/W] | 350.0 | 350.0 | 350.0 | 350.0 | 350.0 | 350.0
p_rated [MW] | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0
Nwt | 60.0 | 60.0 | 0.0 | 0.0 | 30.0 | 30.0
wind_MW_per_km2 [MW/km2] | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0
solar_MW [MW] | 0.0 | 0.0 | 300.0 | 300.0 | 150.0 | 150.0
surface_tilt [deg] | 50.0 | 50.0 | 50.0 | 50.0 | 50.0 | 50.0
surface_azimuth [deg] | 180.0 | 180.0 | 180.0 | 180.0 | 180.0 | 180.0
DC_AC_ratio | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
b_P [MW] | 0.0 | 0.0 | 0.0 | 0.0 | 60.0 | 60.0
b_E_h [h] | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0
cost_of_battery_P_fluct_in_peak_price_ratio | 5 | - | 5 | - | 5 | -
NPV_over_CAPEX | 0.71 | 0.61 | 0.35 | 0.32 | 0.56 | 0.56
NPV [MEuro] | 204.53 | 164.48 | 51.1 | 47.47 | 127.87 | 121.6
IRR | 0.12 | 0.11 | 0.09 | 0.08 | 0.11 | 0.11

## Slide 5: Evaluation results comparison Site: France good wind site
 | Design 1 NEW | Design 1 OLD | Design 2 NEW | Design 2 OLD | Design 3 NEW | Design 3 OLD
LCOE [Euro/MWh] | 20.82 | 23.13 | 30.39 | 30.03 | 24.08 | 26.22
CAPEX [MEuro] | 289.25 | 270.54 | 147.71 | 147.71 | 228.34 | 218.98
OPEX [Meuro] | 5.52 | 5.28 | 2.03 | 2.03 | 3.78 | 3.66
Wind CAPEX [MEuro] | 229.29 | 210.58 | 0 | 0 | 114.65 | 105.29
Wind OPEX [MEuro] | 5.52 | 5.28 | 0 | 0 | 2.77 | 2.65
PV CAPEX [MEuro] | 0 | 0 | 99.5 | 99.5 | 49.75 | 49.75
PV OPEX [MEuro] | 0 | 0 | 2.03 | 2.03 | 1.01 | 1.01
Batt CAPEX [MEuro] | 0 | 0 | 0 | 0 | 10.41 | 10.41
Batt OPEX [MEuro] | 0 | 0 | 0 | 0 | 0 | 0
penalty lifetime [MEuro] | 0 | 0 | 0 | 0 | 0 | 0
AEP [GWh] | 1286.35 | 1111.34 | 412.84 | 414.6 | 856.9 | 765.12
GUF | 0.49 | 0.42 | 0.16 | 0.16 | 0.33 | 0.29
grid [MW] | 300 | 300 | 300 | 300 | 300 | 300
wind [MW] | 300 | 300 | 0 | 0 | 150 | 150
solar [MW] | 0 | 0 | 300 | 300 | 150 | 150
Battery Energy [MWh] | 0 | 0 | 0 | 0 | 180 | 180
Battery Power [MW] | 0 | 0 | 0 | 0 | 60 | 60
Total curtailment [GWh] | 0 | 0 | 0 | 0 | 0.03 | 0.03

## Slide 6: Evaluation results comparison Site: France good wind site
 | Design 1 NEW | Design 1 OLD | Design 2 NEW | Design 2 OLD | Design 3 NEW | Design 3 OLD
Awpp [km2] | 42.86 | 42.86 | 0 | 0 | 21.43 | 21.43
Rotor diam [m] | 134.87 | 134.87 | 134.87 | 134.87 | 134.87 | 134.87
Hub height [m] | 77.43 | 77.43 | 77.43 | 77.43 | 77.43 | 77.43
Number_of_batteries | 0 | 0 | 0 | 0 | 1 | 1